SECTION 28 13 00 ACCESS CONTROL

TELEPHONE ENTRY & ACCESS CONTROL SYSTEMS

DoorKing 1830-90 Series

Display hidden notes.  (File – Options – Display – Hidden Notes)

This specification is based on products from DoorKing, Inc.

120 S. Glasgow Ave.

Inglewood, CA  90301

Tel:  800-826-7493

Fax:  310-641-1586

Email:	info@doorking.com

Web:		www.doorking.com

DoorKing (DKS) was founded in 1948.  The company is one of the largest and oldest manufacturers of access control and vehicular gate operator products in the United States and offers a full line of residential, commercial and industrial products to meet the needs of Architects, Designers, Engineers and Specifiers in almost any design or conceptual plan.  DoorKing is a registered provider of the American Institute of Architects continuing education system.  For learning objectives and to schedule a Lunch & Learn, please send a request to awright@doorking.com.  For a complete library of CSI format 3-part specs, CAD and BIM product renderings, visit doorking.com/architects-specifiers.

PART 1 GENERAL

1.1	WORK INCLUDED

A.	Furnish and install a complete microprocessor controlled, PC Programmable "full-duplex" circuitry voice communication, telephone entry and multi-door access control system as described herein and shown on the plans.  The system shall include all necessary boards, power supplies, keypads, loudspeakers, special mounting boxes, cable, connectors, and accessories for a complete operational communication system.

B.	Scope of work shall include communication and (as required) card, digital or RF transmitter access control for up to 3000 users and up to 8000 card access device codes.

1.2	CONTRACT DOCUMENTS

A.	All equipment and work specified in this section shall comply, with all the General Conditions of the specifications, contract documents, and drawings as indicated.

1.3	RELATED WORK

A.	Contractor shall coordinate all work with other contractors and trades where necessary.

B.	All necessary conduit, raceways, pull boxes, standard boxes, (and special boxes provided by intercom manufacturer), shall be installed by the electrical contractor.

C.	Installation of the communication/access systems shall be coordinated with the installation of other related systems.

1.4	QUALITY ASSURANCE

A.	Installation shall comply with all applicable codes.

B.	All equipment shall be new, in current production, and the standard products of a manufacturer of telephone entry system equipment.

C.	Manufacturer shall guarantee availability of parts, for a minimum of 7-years from date of shipment.

D.	If required, manufacturer shall be able to demonstrate features, functions and operating characteristics.

E.	System shall be installed by a factory authorized contractor, with technicians specifically trained in this system.

F.	On-site maintenance and repair service shall be available locally and within 4-hours, of notification for emergency condition.

G.	System shall interface with other DoorKing systems to allow remote PC programming.

1.5	REFERENCE STANDARDS

A.	Underwriter Laboratories Inc. (UL), UL 294

B.	Telephone Entry System shall be tested for compliance to UL 294 and shall be LISTED by a Nationally Recognized Testing Laboratory (NRTL).

C.	Federal Communications Commission (FCC).

D.	Department of Commerce (DOC) (CAN).

1.6	SUBMITTALS

A.	Provisions:  Comply with Section 01300 SUBMITTALS.

B.	Shall include an equipment list, and data sheet, system description and block diagrams on equipment to be finished.

C.	Shall include all data necessary to evaluate design, quality, and configuration of proposed equipment and system(s).

1.7 	WARRANTY

A.	Systems shall include a factory warranty that equipment is free from defects in design, material, manufacturing and operation.

B.	Factory warranty period shall be for two (2) years parts and workmanship; 24-months from date of shipment. Manufacturer shall not be responsible for improper use, handling, or installation of the product.

C.	Installing communications contractor shall guarantee the equipment, wire, cable, and installation for 12-months from date of acceptance.

PART 2 - PRODUCTS

2.1	ACCEPTABLE MANUFACTURERS

A.	The system as described herein, is based on the 1830-90 Series Telephone Entry & Access Control PC Programmable system manufactured by DoorKing, Inc., Inglewood, California. The 1830-90 series system specified meets requirements of the specifications and shall be considered as the acceptable Base Bid.

B.	Substitutions must meet requirements of Prior Approval, as outlined in the contract documents.  Substitutions that meet Prior Approval requirements must be listed as alternates by addendum, and shall be shown separately on the bid forms.  Consideration will be based on ability to comply with all aspects of the specifications, the desired functional operation, quality, reliability, design, size, and appearance of the equipment, and the support capabilities of the manufacturer.

2.2	SYSTEM DESCRIPTION

A.	The telephone entry & access control system shall provide full duplex hands-free voice communication from the entry location to the resident telephones or cell phones.  Half duplex or simplex type communication will not be allowed.

B. The system shall be capable of storing up to 3000 user names and phone numbers (all models), and up to 8000 card, digital, and/or RF transmitter  access codes (exception: model 1834).

C. The system transaction buffer shall store up to 8000 events.

D. The system shall be capable of being programmed via a personal computer and DoorKing Remote Account Manager for Windows software (free download from doorking.com web site).  Several different methods of connection to the system shall be made available:

1.	Internet

2.	Cellular

3.	POTS (Plain Old Telephone Service)

See Section 2.4.C.

E.	The system shall provide for live streaming of data, displaying live transactions on the computer and shall be able to download the transaction buffer to the PC for analysis.

F.	The system shall be capable of independently controlling a main entry access point plus an additional two (non-communicating) access points.  With 'Tracker Expansion', the system shall be able to control a main entry point plus up to 24 additional (non-communicating) access points (exception: model 1834).

See Section 2.4.A.

G.	Resident names shall be automatically sorted and shall be displayed in alphabetical order on the built-in LCD directory with minimum 1/2 inch characters (1834, 1835 and 1837 only).

H.	System (except 1833) shall incorporate “A” and “Z” buttons to allow guests to scroll through the resident directory.

1. The system shall be designed so that when either the "A" or "Z" button is pressed, the paging shall start in the center of the resident database to reduce search time.

2. Holding the "A" button down will cause the system to rapidly page from the center to the beginning of the resident database.

3.	Holding the "Z" button down will cause the system to rapidly page from the center to the end of the resident database.

4.	Depressing the "A" or "Z" buttons momentarily will cause the system to display one name (1834/1835) or page (1837) at a time.

I.	System (except 1833) shall incorporate a “CALL” button to initiate communication with the resident displayed in the system directory.

J.	Directory codes shall be programmable from one (1) to four (4) digits.

K.	Tone-open numbers to grant guest access shall be programmable.

L.	31 security levels shall restrict user access to specific entry locations, at specific times and days as programmed in the software (exception: model 1834)

M.	32 Holiday Schedules shall be user programmable.

N.	The system shall be capable of providing “True” anti-pass back in 3 different modes of operation (exception: model 1834):

1.	Passive mode shall report anti-pass back violations but will allow entry or exit.

2.	Active mode shall report anti-pass back violations and will not allow entry or exit.

3.	Trap mode shall report anti-pass back violations and will allow entry but not exit.

O.	The system shall have an “Import / Export” feature to allow database transfer between to or from common spreadsheet programs.

P.	Eight (8) hold open time zones shall allow designated access points to be 'un-locked' at times and days as required.

Q.	The system shall be capable of elevator control to restrict user and guest access to floors as programmed in the software (exception: model 1834). Elevator control requires the use of the DoorKing 2348-010 Elevator Control Board, and shall be capable of controlling up to eight (8) elevators, with each elevator serving up to 64 floors.

See Section 2.4.B.

R.	Additional telephone entry systems can share the same user database to control additional access points.

S.	A provision for postal lock input shall allow and record entries by post office personnel.

T.	Access Control Devices: compatible with standard 26-bit wiegand access devices (exception: model 1834):

1.	RF transmitter access requires the use of DoorKing Model 8040 RF receiver, and the use of DoorKing MicroPlus or MicroClik transmitters with 1, 2, 3 or 4 button as required (4-button available with MicroPLUS only).

2.	Card access may be provided by proximity card readers and their respective cards.

3.	Digital entry codes require the use of DoorKing wiegand keypad.

U.	Cabinet

1.	Cabinet is constructed from 16-gauge steel and is dual lockable, gasketed, NEMA 4 rated enclosure.

2.	The cabinet shall accommodate and provide space for a card reader (DK part numbers 1815-302, 1815-380, 1815-215 only), IP camera and TCP-IP adapter (for optional internet connection).

3.	The speaker holes shall be offset to protect the speaker from vandalism.

4.	The system shall utilize LED backlit metal keypad and metal push buttons.

5.	The control board shall be mounted to the rear of the system enclosure to protect it from vandalism.

6.	The stainless steel faceplate shall be reinforced with a galvanized steel sub-plate. Faceplate shall be non-magnetic steel alloy #304 or #316 as per ASTM A167, A176, A408, and A484.

7.	Optional 10-guage hood to enhance vandal resistance.  Specify stainless steel (1814-180) or Black (1815-185).

8.	Optional flush mount kit (rough-in box + stainless steel trim ring).

V.	Dimensions:

1. 1830-90 Series; 14.75 inches high, 12.75 inches wide, 3.75 inches deep.

2.	Hood enclosure (optional); 14.88 inches high, 13.08 inches wide, 5.61 inches deep.

3.	Flush Mount Kit (Optional); 17.27 inches high, 15.34 inches wide, 3.76 inches deep.

2.3	EQUIPMENT

Select access system model. Delete two of the following three items (A-B-C).

Note to Specifier:  Model 1834 has no expansion capabilities and is typically used in applications to control a single access point.  Models 1835 and 1837 can expand wirelessly to control up to 24 access points.  Model 1835 uses a single-line directory display and model 1837 uses an eight-line directory display.

A.	Model 1834-090 Telephone Entry System.

1.	Controls two access points.

2.	Single-line LCD directory.

3.	A-Z scroll buttons.

4.	CALL button.

B.	Model 1835-090 Telephone Entry and Access Control System.

1.	Controls three access points.

2.	Expandable to control up to 24 access points.

3.	Elevator control expansion.

4.	Single-line LCD directory.

5.	A-Z scroll buttons.

6.	CALL button.

C.	Model 1837-090 Telephone Entry and Access Control System.

1.	Controls three access points.

2.	Expandable to control up to 24 access points.

3.	Elevator control expansion.

4.	Eight-line LCD directory.

5.	A-Z scroll buttons.

6.	CALL button.

2.4 	OPTIONS

The following paragraphs are optional items.  Delete if not required.

A.	Tracker expansion boards (p/n 2358-010).

Tracker expansion boards are used when more than three (3) entry points need to be controlled.  Tracker expansion boards also provide door ajar and forced entry alarms.  One (1) tracker board is required for each entry point to be controlled.

1. Tracker board NEMA 4 rated enclosures.

Enclosures can be mixed and matched.  For example, if eight tracker 	boards are used, two quad enclosures, eight single enclosures or one 	quad enclosure and four single enclosures can be used.  The number 	and type of enclosures are usually determined by the installer at 	the time of installation.

a. Single (p/n 2351-080)

b. Quad (2351-085)

c. Quad Pre-wired (2351-082)

2. 900 MHz Wireless Connection for Tracker Expansion Boards.

Rather than hard wiring the tracker expansion boards to the 1830-90 	series system controller, the connection can be made wirelessly.  	One (1) base kit is required, which is installed in the 1830-90 	series controller. Each tracker expansion boards requires a wireless 	kit.  For example, if eight tracker boards are used, one (1) 2333-	080 is required and eight (8) 1470-080 kits are required.

a. Wireless base kit, one (1) required (P/N 2333-080)

b. Wireless tracker kit (P/N 1470-080)

c. Dual channel repeater, optional (P/N 2332-080)

B.	Elevator control boards (p/n 2348-010).

Elevator control boards are used to control which elevators and/or floors users or visitors have access to.  Each elevator control board can control up to 16 floors.  A maximum of four (4) elevator control boards can be connected to a single elevator to control up to 64 floors.  A maximum of eight (8) elevators can be controlled in this manner.

i. Elevator control board NEMA 4 rated enclosures.

Enclosures can be mixed and matched.  For example, if eight elevator 	boards are used, one quad enclosure and two dual enclosures; or two 	quad enclosures; or four dual enclosures can be used.  The number 	and type of enclosures are usually determined by the installer at 	the time of installation.

a. Dual (p/n 2348-080)

b. Quad (p/n 2348-081)

C.	Connection options

One (1) of the following three options is required.

1.	Internet (VoIP) requires DoorKing P/N 2334-080 (VoIP subscription 	required).

2.	Cellular requires DoorKing P/N 1800-080 (cellular subscription 	required).

3.	POTS (Plain Old Telephone Service).

NOTE to specifier: Because of changes being made to the PSTN (Public 	Switched Telephone Network), DoorKing does not recommend and cannot 	guarantee programming of the system via a POTS line and modem any 	longer.

D.	Programming options

One (1) of the following two options is required.

1.	DKS Cloud programming allows remote programming via a laptop, tablet or smartphone from anywhere with an internet connection.

2.	Dedicated PC – Requires Remote Account Manager software to be installed on the PC (free download from doorking.com).

NOTE to specifier: DKS Cloud programming is included with a VoIP or 	cellular subscription.

E. Mounting accessories (optional).

Mounting accessories simplify installation and can cosmetically enhance the look.  The hooded enclosure also helps protect the system against vandalism.  The manufacturer recommends the use of the flush mounting kit whenever the flush mount design is specified.  Delete two of the following three items (i, ii, iii).

i.	10-guage hooded enclosure stainless steel (p/n 1814-180).

ii.	10-guage hooded enclosure black (p/n 1814-185).

iii.	Flush mount kit (p/n 1814-200).

PART 3 - EXECUTION

3.1	INSTALLATION

A.	It is preferred that this product be installed by a qualified technician who is certified by the Institute of Dealer Education and Accreditation (IDEA) or the American Fence Association (AFA).

B. Wiring shall be uniform and in accordance with national electric codes and manufacturers instructions.

C.	Conform to the manufacturers written requirements for installation.

D. Equipment shall be firmly secured, plumb, and level.

E.	All splices shall be in easily accessible junction boxes or on terminal boards.

F.	All cable runs at the main control cabinets, in all auxiliary cabinets and at all phone blocks shall be tagged and identified.

G.	Coordinate all work with other effected trades and contractors.

H.	Fastenings:

1.	Fasten on gypsum board wall surfaces with screws into wood or metal blocking, or with bolts or molly anchors, not less than 1/4" diameter.  Screwing into gypsum board or plaster with plugs will not be acceptable.

2.	Fasten into concrete or masonry with self-drilling masonry anchors Phillips Redhead, Bulldog or Rawl Sabertooth.

3.2	SYSTEM INITIALIZING AND PROGRAMMING

A.	System shall include all software and/or instructions necessary for system configuration.

B.	System shall be turned on and adjustment made to meet requirements of specifications and on-site conditions.

C.	System shall be programmed to function as specified.

D.	Directory numbers, feature codes, and special programming shall be documented, printed and made available to all owners.

3.3	SYSTEM TEST PROCEDURES

A.	System shall be completely tested to assure that the exchange and all components, stations, speakers, and accessories are hooked-up and in working order.

B.	System shall be pre-tested by contractor and certified to function in accordance with plans and specifications.

C.	System shall be tested in presence of owner's representative.

3.4	OWNER INSTRUCTIONS

A.	Installation contractor shall conduct up to (4) hours of instruction in use and operation of the system to designated owner representatives, within (30) days of acceptance.

B.	Installation contractor shall conduct up to (4) hours of technical training, in programming, troubleshooting, and service of the system, to designated owner representatives within (90) days of system acceptance.

3.6	MANUALS AND DRAWINGS

A.	Contractor shall provide owner with (2) copies of standard factory prepared operation, installation and maintenance manuals.  Manuals shall include typical wiring diagrams.

B.	Contractor shall provide owner with (2) copies of any risers, layouts, and special wiring diagrams showing any changes to standard drawings, if required on project.

END OF SECTION